## Sheet1
CONDUCTOR DATA AND PARAMATERS
Type of Conductor: | ACSR_GZ | ACSR_GZ BRITISH
Conductor Name: | LEMON | DOG
Voltage (kV): | 132 | 132
Number of Conductors Per Phase: | 1 | 1
Ambient Temperature (oC): | 40 | 40
Maximum Operating Temperature (oC): | 85 | 85
Wind Speed (m/s): | 4.1 | 4.1
ψ - Wind Attack Angle (o): | 90 | 90
Conductor Surface Condition: | Rural Weathered | Rural Weathered
Ground Condition: | Soil, Grass and Crops | Soil, Grass and Crops
Time of Day: | Summer Noon | Summer Noon
Rating Wind Attack Angle
|  | 0 Degrees |  | 15 Degrees |  | 30 Degrees |  | 45 Degrees |  | 60 Degrees |  | 75 Degrees |  | 90 Degrees
Line | Conductor | Amps (A) | MVA | Amps (A) | MVA | Amps (A) | MVA | Amps (A) | MVA | Amps (A) | MVA | Amps (A) | MVA | Amps (A) | MVA
PIC-CAP 71 | LEMON | 622 | 142 | 734 | 168 | 827 | 189 | 891 | 204 | 935 | 214 | 962 | 220 | 970 | 222
PIC-CAP 72 | LEMON | 622 | 142 | 734 | 168 | 827 | 189 | 891 | 204 | 935 | 214 | 962 | 220 | 970 | 222
PIC-BSN 71 | LEMON | 622 | 142 | 734 | 168 | 827 | 189 | 891 | 204 | 935 | 214 | 962 | 220 | 970 | 222
PIC-BSN 72 | DOG | 376 | 86 | 444 | 101 | 500 | 114 | 538 | 123 | 565 | 129 | 581 | 133 | 587 | 134